## BOARD OF TECHNICAL EDUCATION

PORVORIM-GOA

November, 2012 Examinations

Programme: Electrical Engg.

Subject: Testing & Maintenance of Electrical Equipments(5104)

# Time Duration: 3 Hrs.                                               Max. Marks:  75

Instructions: 1) All Questions are compulsory.

2) Figures to the right indicate full marks.

3) Assume suitable additional data if required.

| Q.No.1. | Answer any five of the following Questions: | 5 x 3 = 15 |
| --- | --- | --- |
| a) | State any two points of distinction between type test & routine test. |  |
| b) | What do you mean by regenerative testing? State it advantages & disadvantages. |  |
| c) | Justify the statements- “Generally large capacity machines are tested by indirect method of testing”. |  |
| d) | What is the essential difference between the sustained three phase short circuit & sudden three phase short circuit test on synchronous machine? |  |
| e) | What are the various type of no load losses taking place in three phase induction motor? How these losses are separated? |  |
| f) | Explain in brief vacuum impregnation process of revarnishing machine winding. |  |
| g) | Enlist various methods of measurement of temperature rise of transformer winding. |  |
| Q.No.2. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Enlist various losses occurring in a dc machine as per IS classification. Also state the parameter on which each one depends. |  |
| b) | Hpkinson’s test on 2 shunt machines gave the following results: Line voltage = 460 V Motor armature current = 500A Line current = 80A Field current of machines is 5A & 6A, armature resistance of each machine is 0.015. Calculate the efficiency of the machine. |  |
| c) | A DC shunt generator delivers 195A at a terminal potential difference of 250V. The armature resistance & field resistance are 0.02 & 50 respectively. The iron & frictional losses equal 950W. Find - Emf generated - Cu losses - O/p of prime mover - Mechanical efficiency, electrical efficiency & overall efficiency. |  |
| Q.No.3. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | How insulation resistance is measured for power transformer? What are the minimum permissible values of insulation resistance of transformer winding. |  |
| b) | Determine the ranges of measuring instruments required for performing Sumpman’s (Back to back) test on Transformer of the following ratings: 25KVA, 3 phase, 50Hz, 11KV/400V, YY connected. |  |

………2/-

-2-

| c) | It is required to know the hysteresis & eddy current losses of a transformer separately. What are the tests necessary? Explain how the test data will be used to compute these losses. |  |
| --- | --- | --- |
| Q.No.4. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Briefly explain phasing out & polarity test performed on a 3 phase Transformer. |  |
| b) | State and explain the methods of measurement of temperature rise of various parts of Induction motor. |  |
| c) | An induction motor rated at 3.7KW, 415V, 1440 rpm, 7.8A is connected permanently in delta. The winding resistance is measured at 30ºC & is found to be 2 between two terminals of motor. Determine the copper losses in motor at full rated current & working temperature of 105ºC. |  |
| Q.No.5. | Answer any two of the following Questions: | 2 x 6 = 12 |
| a) | Explain the no load test & blocked rotor test on three phase Induction motor. |  |
| b) | Describe the following tests for induction motor: - High voltage test - Resistance measurement test. |  |
| c) | State & explain different types of losses occurring in synchronous machine. Explain how any one of these losses is determined. |  |
| Q.No.6. | Write short notes on two of the following: | 2 x 6 = 12 |
| a) | Maintenance schedule of transformer as per I.S. |  |
| b) | Commissioning tests on polyphase induction motor |  |
| c) | Care of electrical equipment during period of inactivity & storage |  |

***********